## Lab Report - January 2023
32.4 MLD WWTP, Guheshwori | [18 empty] | 32.4 MLD WWTP, Guheshwori | [16 empty] | 32.4 MLD WWTP, Guheshwori | [13 empty] | 32.4 MLD WWTP, Guheshwori | [12 empty] | 32.4 MLD WWTP, Guheshwori | [10 empty] | 32.4 MLD WWTP, Guheshwori | [14 empty] | 32.4 MLD WWTP, Guheshwori
KATHMANDU, NEPAL | [18 empty] | KATHMANDU, NEPAL | [16 empty] | KATHMANDU, NEPAL | [13 empty] | KATHMANDU, NEPAL | [12 empty] | KATHMANDU, NEPAL | [10 empty] | KATHMANDU, NEPAL | [14 empty] | KATHMANDU, NEPAL
Project No: | 10M170 | [13 empty] | Month: | 2023-01-01 |  |  | Project No: | 10M170 | [10 empty] | Month: |  |  | 2023-01-01 |  | Project No: | 10M170 | [8 empty] | Month: | 2023-01-01 |  |  | Project No: |  | 10M170 | [6 empty] | Month: | 2023-01-01 |  |  | Project No: | 10M170 | [6 empty] | Month: | 2023-01-01 |  | Project No: |  | 10M170 | [7 empty] | Month: | 2023-01-01 |  |  |  | Project No: | 10M170 | [9 empty] | Month: | 2023-01-01
Date | Power Generation and Consumption |  |  |  | Inlet | [13 empty] | Date | Grit Classifier Outlet | Primary Clarifier |  |  |  |  | Secondary Clarifier |  |  |  |  | Secondary Sedimentation tank Outlet |  |  |  |  | Date | CHLORINE CONTACT TANK (Composite) | [5 empty] | CHLORINE CONTACT TANK | [6 empty] | Aeration Tank | [12 empty] | Digester Sludge Feeding Details | [10 empty] | Digester Performance Details | [14 empty] | Digester Outlet |  |  |  | Centrifuge |  |  | Bio Gas |  |  | Scrubber |  | Odour Control Unit
| Power Generation from Gas Engine | Daily Power Consumption from NEA (MW) | Total Power Consumption from NEA & GE (MW) | Total Power (KWh)/Flow (ML) | Raw Sewage Flow | Raw Sewage (Composite) | [5 empty] | Raw Sewage | [37 empty] | DATE | Existing Aeration Tank | [5 empty] | New Aeration Tank | [5 empty] | DATE | Primary sedimentation tank Underflow |  |  | Thickener Sludge Parameters | [6 empty] | DATE | Digester - A | [6 empty] | Digester - B | [6 empty] | DATE | Centrifuge Feed |  |  | Centrifuge Cake |  | Centrifuge Feed Totalizer | Gas Generation | Methane | Carbon Dioxide | Inlet | Outlet
[6 empty] | pH | BOD5 | COD | TSS | NH3-N | O & G | pH | BOD5 | COD | TSS | PO4 | Total Coliform | Fecal coliform |  | TSS | PH | TSS | BOD5 | COD | PST Sludge Totalizer | PH | TSS | BOD5 | COD | Existing RAS | PH | TSS | BOD5 | COD | New RAS |  | pH | BOD5 | COD | TSS | O & G | Ammonical Nitrogen | pH | BOD5 | COD | TSS | Total Coliform | Fecal coliform | FRC |  | PH | DO | MLSS | MLVSS | SV30 | SVI | PH | DO | MLSS | MLVSS | SV30 | SVI |  | pH | TS | VS | pH | TS | VS | VFA | Alkalinity | VFA/ Alkalinity Ratio | Digester Feed Totalizer |  | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp |  | PH | TS | VS | TS | VS |  |  | CH4 | CO2 | H2S | H2S | Inlet pH | Outlet pH
Control Limits |  |  |  |  | 32.4 | 6.0 - 9.0 | 300 | 800 | 400 | 79 | 120 | 6.0 - 9.0 | 300 | 800 | 400 | 12 | 107-109 | 106-107 | Control Limits | - | [15 empty] | Control Limits | 6.5-8.0 | < 10 | < 250 | < 10 | < 10 | < 50 | 6.5-8.0 | < 10 | < 250 | < 10 | < 500 | < 100 | Max 1 | Control Limits | - | > 0.5 | - | - | - | - | - | > 0.5 | - | - | - | - | Control Limits | [10 empty] | Control Limits | [14 empty] | Control Limits
Units | MW | <482.02 KWh / ML of Treated Water |  |  | MLD | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Units | mg/L | - | mg/L | mg/L | mg/L | m3 | - | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | Units | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | MPN /100ml | MPN /100ml | mg/L | Units | - | mg/L | mg/L | mg/L | ml/L | - | - | mg/L | mg/L | mg/L | ml/L | - | Units | - | % | % | - | % | % | mg/l | mg/l | - | m3 | Units | - | % | % | mg/l | mg/l | - | 0C | - | % | % | mg/l | mg/l | - | 0C | Units | - | % | % | % | % | m3 | Nm3 | % | % | ppm | ppm | - | -
2023-01-01 | 1.3 | 10.93 | 12.23 | 630.7375 | 19.39 | 7.01 | 419.5 | 679 | 470 | 75.6 | 85 | 7.04 | 449 | 749 | 495 | - | 56000000 | 35000000 | 2023-01-01 | 590 | 6.92 | 470 | 389 | 549 | 272 | 6.75 | 19 | 12.8 | 45 | 9660 | 6.81 | 16 | 12.2 | 63 | 11710 | 2023-01-01 | 7.3 | 9.4 | 56 | 13.3 | 5 | 14 | 7.01 | 8.3 | 42 | 12.6 | 660 | 370 | 0.2 | 2023-01-01 | 6.655 | 1.015 | 5455 | 3395 | 630 | 114.971 | 6.72 | 1.215 | 6430 | 3875 | 795 | 124.1569 | 2023-01-01 | 6.59 | 4.1475 | 47.47 | 6.42 | 4.54 | 54.21 | 744 | 375 | 1.984 | 162 | 2023-01-01 | 6.96 | 5.51 | 43.76 | 1164 | 1675 | 0.69493 | 22.01 | 6.84 | 5.99 | 41.45 | 1032 | 1700 | 0.60706 | 18.34 | 2023-01-01 | 6.81 | 5.13 | 45.95 | 23.87 | 49.99 | 176 | - | - | - | 566 | 170 | 7.02 | 3.27
2023-01-02 | 1.1 | 12.34 | 13.44 | 678.3083 | 19.814 | 7.14 | 494 | 581 | 520 | 72.8 | 43 | 7.39 | 569.5 | 773 | 665 | - | 48000000 | 23000000 | 2023-01-02 | 790 | 7.13 | 1685 | 404.5 | 504 | 269 | 6.98 | 20 | 16.3 | 59 | 8800 | 7 | 23 | 15.7 | 52 | 11210 | 2023-01-02 | 7.15 | 9.2 | 63 | 12.3 | 3.5 | 16.8 | 7.19 | 9.1 | 49 | 14 | 880 | 450 | 0.5 | 2023-01-02 | 7.535 | 1.015 | 6145 | 3845 | 690 | 111.9469 | 7.46 | 0.825 | 7015 | 4205 | 825 | 117.9804 | 2023-01-02 | 6.525 | 4.1025 | 54.2275 | 6.42 | 5.16 | 53.78 | 780 | 350 | 2.2286 | 186 | 2023-01-02 | 6.89 | 5.9 | 47.23 | 1008 | 1650 | 0.61091 | 22.08 | 6.8 | 5.75 | 44.16 | 1092 | 1600 | 0.6825 | 18.23 | 2023-01-02 | 6.77 | 4.58 | 44.57 | 20.24 | 50.88 | 176 | - | - | - | 453 | 141 | 7.08 | 3.51
2023-01-03 | 1.3 | 11.19 | 12.49 | 723.4289 | 17.265 | 7 | 434.1 | 679 | 510 | 86.8 | 106 | 7.06 | 509 | 658 | 610 | - | 58000000 | 11000000 | 2023-01-03 | 650 | 7.02 | 1230 | 464 | 553 | 247 | 6.79 | 25 | 18.2 | 84 | 9170 | 6.82 | 16 | 12.8 | 77 | 15620 | 2023-01-03 | 7.35 | 9 | 52 | 12 | 9 | 14 | 7.02 | 7.4 | 56 | 14.6 | 900 | 220 | 0.5 | 2023-01-03 | 6.595 | 1.005 | 6105 | 3480 | 635 | 102.516 | 6.695 | 0.99 | 7320 | 4215 | 835 | 114.4992 | 2023-01-03 | 6.5075 | 3.8125 | 62.0525 | 6.44 | 5.29 | 57.39 | 732 | 525 | 1.3943 | 160 | 2023-01-03 | 6.87 | 4.91 | 44.97 | 1320 | 1525 | 0.86557 | 22.15 | 6.79 | 5.52 | 45.16 | 1176 | 1500 | 0.784 | 18.45 | 2023-01-03 | - | - | - | - | - | 123 | - | - | - | 566 | 141 | 7.04 | 3.42
2023-01-04 | 1.2 | 10.61 | 11.81 | 696.7552 | 16.95 | 7.01 | 359 | 861 | 370 | 47.6 | 69 | 7.24 | 449.1 | 780 | 580 | - | 69000000 | 31000000 | 2023-01-04 | 425 | 7.05 | 720 | 524.1 | 430 | 272 | 7.01 | 22 | 16.5 | 91 | 6770 | 7.03 | 24 | 16.5 | 98 | 8180 | 2023-01-04 | 7.35 | 7.7 | 59 | 11.67 | 8.5 | 19.6 | 7.15 | 9.6 | 56 | 11 | 970 | 550 | 0.2 | 2023-01-04 | 6.675 | 0.93 | 5880 | 3705 | 705 | 120.9054 | 6.865 | 0.85 | 7325 | 4965 | 870 | 118.852 | 2023-01-04 | 6.4725 | 4.635 | 54.2725 | 6.6 | 4.7 | 53.91 | 900 | 475 | 1.8947 | 190 | 2023-01-04 | 6.97 | 4.78 | 44.19 | 1260 | 1575 | 0.8 | 22.67 | 6.91 | 5.92 | 42.54 | 1128 | 1675 | 0.67343 | 18.35 | 2023-01-04 | 6.88 | 4.91 | 42.95 | 21.16 | 42.56 | 168 | - | - | - | 453 | 113 | 6.39 | 2.17
2023-01-05 | 1.3 | 11.12 | 12.42 | 711.9518 | 17.445 | 6.89 | 373.7 | 780 | 575 | 53.4 | 76 | 7.3 | 494 | 857 | 515 | - | 52000000 | 29000000 | 2023-01-05 | 705 | 7.2 | 330 | 299 | 318 | 263 | 7.15 | 20 | 15.8 | 63 | 9010 | 7.12 | 26 | 17 | 87 | 7830 | 2023-01-05 | 7.73 | 9.8 | 56 | 13 | 5.5 | 22.4 | 7.34 | 6.5 | 38 | 12.4 | 910 | 470 | 0.2 | 2023-01-05 | 6.785 | 0.69 | 6055 | 3895 | 875 | 144.0933 | 6.95 | 0.57 | 7545 | 4915 | 870 | 115.3398 | 2023-01-05 | 6.455 | 3.905 | 55.33 | 6.41 | 5.46 | 49.81 | 888 | 375 | 2.368 | 182 | 2023-01-05 | 6.92 | 5 | 44.39 | 1224 | 1500 | 0.816 | 22.14 | 6.84 | 5.81 | 41.85 | 1272 | 1500 | 0.848 | 18.45 | 2023-01-05 | 6.79 | 3.85 | 46.43 | 21.35 | 44.18 | 152 | - | - | - | 556 | 170 | 7 | 3.19
2023-01-06 | 1.3 | 12.53 | 13.83 | 718.4789 | 19.249 | 7.03 | 509.2 | 784 | 530 | 64.4 | 46.5 | 6.66 | 538.7 | 707 | 640 | - | 44000000 | 17000000 | 2023-01-06 | 455 | 7.1 | 1665 | 358.7 | 672 | 288 | 7.1 | 24 | 17.9 | 80 | 9720 | 7.15 | 23 | 14.3 | 80 | 7970 | 2023-01-06 | 7.42 | 6.7 | 66 | 9.6 | 5.5 | 22.4 | 7.12 | 9.2 | 63 | 14 | 890 | 210 | 0.2 | 2023-01-06 | 7.035 | 0.565 | 6015 | 4080 | 735 | 121.9336 | 6.99 | 1.225 | 7045 | 4780 | 885 | 125.6343 | 2023-01-06 | 6.55 | 3.8475 | 56.565 | 6.49 | 5.04 | 56.33 | 972 | 625 | 1.5552 | 169 | 2023-01-06 | 6.98 | 4.95 | 47.66 | 1188 | 1675 | 0.70925 | 22.56 | 6.92 | 5.45 | 44.77 | 1164 | 1750 | 0.66514 | 17.98 | 2023-01-06 | 6.89 | 4.81 | 47.25 | 22.41 | 49.79 | 172 | - | - | - | 453 | 141 | 6.43 | 3.4
2023-01-07 | 1.4 | 14.62 | 16.02 | 902.0778 | 17.759 | 7.29 | 539.1 | 679 | 665 | 58 | 43.5 | 6.91 | 614.2 | 899 | 825 | - | 51000000 | 21000000 | 2023-01-07 | 715 | 6.99 | 655 | 464.2 | 654 | 386 | 6.99 | 9 | 7.6 | 73 | 10340 | 7.09 | 12 | 9.4 | 91 | 15620 | 2023-01-07 | 7.03 | 6.3 | 42 | 8.3 | 5 | 10 | 7.21 | 6.4 | 49 | 7 | 770 | 180 | 0.5 | 2023-01-07 | 7.08 | 0.9 | 5890 | 3655 | 805 | 136.6108 | 6.935 | 0.865 | 6625 | 4095 | 825 | 124.5528 | 2023-01-07 | 6.5425 | 4.065 | 54.6575 | 6.47 | 5.1 | 54.05 | 804 | 450 | 1.7867 | 211 | 2023-01-07 | 6.96 | 4.9 | 45.28 | 1020 | 1650 | 0.61818 | 22.97 | 6.91 | 5.5 | 44.02 | 1128 | 1650 | 0.68364 | 17.86 | 2023-01-07 | 6.89 | 4.31 | 42.63 | 20.33 | 53.81 | 180 | - | - | - | 566 | 170 | 6.57 | 2.86
2023-01-08 | 0.8 | 15.29 | 16.09 | 923.227 | 17.428 | 7.05 | 509 | 791 | 580 | 52 | 63.5 | 7.53 | 569.1 | 787 | 670 | - | 42000000 | 10000000 | 2023-01-08 | 415 | 7.49 | 1080 | 449.1 | 560 | 370 | 6.43 | 13 | 11.1 | 66 | 9660 | 6.51 | 16 | 11.7 | 80 | 14570 | 2023-01-08 | 6.88 | 7.1 | 56 | 8.7 | 6.5 | 8 | 6.4 | 6.3 | 49 | 7 | 640 | Nil | 0.5 | 2023-01-08 | 6.94 | 1.1 | 6050 | 3980 | 820 | 135.54 | 6.745 | 1.155 | 6865 | 4340 | 850 | 123.927 | 2023-01-08 | 6.4875 | 4.2375 | 52.165 | 6.3 | 5.15 | 53.36 | 516 | 475 | 1.0863 | 216 | 2023-01-08 | 6.92 | 4.72 | 43.33 | 1104 | 1500 | 0.736 | 23.34 | 6.8 | 5.51 | 41.4 | 1068 | 1675 | 0.63761 | 17.25 | 2023-01-08 | 6.85 | 5.54 | 41.74 | 21.17 | 48.54 | 164 | - | - | - | 566 | 113 | 6.7 | 3.13
2023-01-09 | 2 | 15.22 | 17.22 | 996.009 | 17.289 | 7.19 | 449.3 | 650 | 550 | 82 | 66.5 | 7.27 | 479 | 801 | 510 | - | 58000000 | 23000000 | 2023-01-09 | 420 | 7.24 | 245 | 239 | 462 | 268 | 6.34 | 15 | 12.2 | 63 | 7530 | 6.26 | 26 | 15.2 | 56 | 11220 | 2023-01-09 | 6.94 | 6.8 | 74 | 8 | 4.5 | 10 | 6.47 | 7.1 | 49 | 9.6 | 560 | 200 | 0.5 | 2023-01-09 | 6.41 | 1.04 | 6170 | 3635 | 825 | 133.7314 | 6.485 | 1.06 | 6780 | 3730 | 820 | 120.9911 | 2023-01-09 | 6.4825 | 3.7825 | 54.9475 | 6.4 | 5.28 | 56.1 | 408 | 625 | 0.6528 | 167 | 2023-01-09 | 6.94 | 5.51 | 46.81 | 1008 | 1775 | 0.56789 | 22.98 | 6.75 | 5.59 | 45.96 | 1224 | 1450 | 0.84414 | 17.11 | 2023-01-09 | 6.98 | 5.73 | 47.36 | 26.01 | 58.5 | 174 | - | - | - | 453 | 113 | 6.36 | 2.94
2023-01-10 | 1.6 | 11.15 | 12.75 | 900.4237 | 14.16 | 7.04 | 509 | 819 | 520 | 108 | 58.5 | 7.15 | 524.3 | 759 | 660 | - | 46000000 | 11000000 | 2023-01-10 | 520 | 7.11 | 960 | 344.3 | 458 | 280 | 6.54 | 15 | 11.9 | 70 | 10160 | 6.69 | 24 | 13.7 | 80 | 15420 | 2023-01-10 | 7.11 | 7.7 | 56 | 9.4 | 3.5 | 24 | 6.81 | 7.1 | 66 | 9.6 | Nil | Nil | 0.2 | 2023-01-10 | 6.73 | 1.025 | 6150 | 3725 | 860 | 140.2959 | 6.465 | 1.065 | 6740 | 4135 | 800 | 119.5521 | 2023-01-10 | 6.5375 | 4.4725 | 53.225 | 6.46 | 5.55 | 53.84 | 576 | 550 | 1.0473 | 232 | 2023-01-10 | 6.97 | 5.5 | 43.06 | 1320 | 1750 | 0.75429 | 22.88 | 6.85 | 5.66 | 45.67 | 1284 | 1475 | 0.87051 | 16.98 | 2023-01-10 | 6.98 | 3.97 | 43.65 | 20.39 | 47.01 | 175 | - | - | - | 566 | 141 | 7.02 | 3.11
2023-01-11 | 1.6 | 14.9 | 16.5 | 959.4139 | 17.198 | 7.01 | 629.1 | 1235 | 935 | 94 | 56 | 7.02 | 614 | 1326 | 1160 | - | 59000000 | 31000000 | 2023-01-11 | 640 | 7 | 1195 | 479 | 742 | 262 | 6.84 | 27 | 20.6 | 108 | 10240 | 6.79 | 30 | 23 | 98 | 13800 | 2023-01-11 | 7.09 | 7.5 | 73 | 9.3 | 4.5 | 36 | 6.99 | 8.3 | 66 | 8.7 | 990 | 260 | 0.2 | 2023-01-11 | 6.455 | 1.03 | 6650 | 4095 | 840 | 126.4927 | 6.56 | 1.075 | 6570 | 4130 | 760 | 115.4401 | 2023-01-11 | 6.2975 | 4.4625 | 55.33 | 6.29 | 5.64 | 52.48 | 804 | 450 | 1.7867 | 189 | 2023-01-11 | 6.77 | 4.87 | 47.9 | 1068 | 1575 | 0.6781 | 22.65 | 6.51 | 5.34 | 46.82 | 1200 | 1350 | 0.88889 | 16.45 | 2023-01-11 | 6.6 | 5.75 | 46.71 | 20.78 | 47.71 | 173 | - | - | - | 453 | 141 | 6.79 | 2.41
2023-01-12 | 1.5 | 13.83 | 15.33 | 906.9933 | 16.902 | 7.08 | 434.1 | 766 | 460 | 84 | 89 | 7.09 | 614.1 | 969 | 645 | - | 9000000 | 4000000 | 2023-01-12 | 410 | 6.99 | 1515 | 404.1 | 535 | 505 | 6.78 | 31 | 17.1 | 101 | 10170 | 6.81 | 25 | 17.7 | 119 | 11660 | 2023-01-12 | 7.14 | 7.5 | 49 | 10.3 | 36 | 4.5 | 7.05 | 8.4 | 66 | 9.6 | Nil | Nil | 0.2 | 2023-01-12 | 6.575 | 0.95 | 6570 | 4180 | 825 | 125.8788 | 6.595 | 0.95 | 6555 | 4320 | 750 | 114.9654 | 2023-01-12 | 6.4725 | 4.43 | 49.3775 | 6.33 | 6.28 | 49.83 | 624 | 425 | 1.4682 | 176 | 2023-01-12 | 6.76 | 5.09 | 45.41 | 1044 | 1475 | 0.7078 | 22.71 | 6.57 | 6.06 | 44.34 | 1116 | 1425 | 0.78316 | 16.01 | 2023-01-12 | 6.63 | 3.8 | 38.49 | 23.1 | 50.45 | 171 | - | - | - | 453 | 170 | 7.07 | 3.11
2023-01-13 | 1.8 | 14.59 | 16.39 | 872.5511 | 18.784 | 7.23 | 524.3 | 780 | 550 | 98 | 101 | 7.01 | 479.1 | 742 | 585 | - | 18000000 | 13000000 | 2023-01-13 | 550 | 6.87 | 810 | 434.1 | 553 | 227 | 6.88 | 21 | 15.9 | 108 | 10760 | 6.82 | 26 | 16.5 | 98 | 12620 | 2023-01-13 | 7.19 | 6.5 | 59 | 8.3 | 5.5 | 44 | 7.47 | 8.1 | 66 | 13.6 | 240 | 60 | 0.2 | 2023-01-13 | 6.895 | 0.895 | 6610 | 4155 | 815 | 123.3087 | 6.545 | 0.99 | 7175 | 4600 | 830 | 115.8017 | 2023-01-13 | 6.31 | 4.4875 | 51.6625 | 6.11 | 5.45 | 52.59 | 852 | 400 | 2.13 | 167 | 2023-01-13 | 6.76 | 5.36 | 46.21 | 1524 | 1225 | 1.2441 | 22.6 | 6.38 | 5.97 | 46.19 | 1044 | 1075 | 0.97116 | 16.45 | 2023-01-13 | 6.53 | 5.26 | 48.07 | 21.54 | 50.13 | 176 | - | - | - | 566 | 170 | 6.83 | 3.2
2023-01-14 | 1.7 | 13.37 | 15.07 | 794.2029 | 18.975 | 7.1 | 434.2 | 1014 | 790 | 90 | 95 | 7.33 | 524.3 | 840 | 680 | - | 14000000 | 5000000 | 2023-01-14 | 580 | 7.08 | 865 | 509.3 | 486 | 265 | 6.65 | 25 | 12.5 | 45 | 10580 | 6.88 | 23 | 13.1 | 63 | 17450 | 2023-01-14 | 7.12 | 5.2 | 45 | 8.3 | 5.5 | 28 | 6.83 | 7.1 | 49 | 8 | 330 | 80 | 0.5 | 2023-01-14 | 7.575 | 0.96 | 6475 | 3675 | 795 | 122.9688 | 7.36 | 0.865 | 7060 | 4520 | 770 | 109.2521 | 2023-01-14 | 6.4425 | 4.3975 | 51.665 | 6.28 | 5.57 | 47.43 | 744 | 475 | 1.5663 | 101 | 2023-01-14 | 6.85 | 4.87 | 49.56 | 1284 | 1475 | 0.87051 | 22.71 | 6.82 | 5.51 | 47.18 | 1212 | 1450 | 0.83586 | 16.4 | 2023-01-14 | 6.6 | - | - | - | - | 149 | - | - | - | 566 | 141 | 7.02 | 3.86
2023-01-15 | 1.6 | 13.68 | 15.28 | 789.1339 | 19.363 | 6.78 | 418.9 | 983 | 700 | 68 | 102 | 7.08 | 524.2 | 941 | 710 | - | 10000000 | 8000000 | 2023-01-15 | 560 | 7 | 675 | 239.2 | 581 | 315 | 6.82 | 13 | 9.4 | 84 | 9570 | 6.89 | 25 | 11.2 | 98 | 13620 | 2023-01-15 | 7.08 | 7 | 31 | 9 | 14 | 9.5 | 6.92 | 4.9 | 66 | 8.6 | 210 | 30 | 0.5 | 2023-01-15 | 6.625 | 0.915 | 6525 | 3620 | 805 | 124.1748 | 6.715 | 0.84 | 7015 | 4390 | 835 | 119.1212 | 2023-01-15 | 6.5075 | 4.505 | 59.9875 | 6.5 | 5.35 | 58.98 | 960 | 525 | 1.8286 | 133 | 2023-01-15 | 6.86 | 5.91 | 45.1 | 1416 | 1625 | 0.87138 | 22.85 | 6.83 | 5.21 | 49.72 | 1344 | 1625 | 0.82708 | 16.23 | 2023-01-15 | 6.91 | 5.29 | 54.39 | 23.78 | 48.72 | 151 | - | - | - | 453 | 113 | 6.82 | 3.03
2023-01-16 | 1.6 | 13.57 | 15.17 | 861.9808 | 17.599 | 7.02 | 449.1 | 1004 | 490 | 72 | 63 | 7.08 | 478.9 | 1014 | 510 | - | 52000000 | 28000000 | 2023-01-16 | 695 | 7 | 590 | 358.9 | 528 | 241 | 6.42 | 28 | 14.5 | 91 | 10600 | 6.62 | 21 | 14.5 | 63 | 15780 | 2023-01-16 | 7.09 | 5.4 | 49 | 8.7 | 11.5 | 20 | 6.69 | 6.7 | 52 | 8.4 | 660 | 240 | 0.2 | 2023-01-16 | 6.285 | 0.84 | 6955 | 4390 | 825 | 118.5536 | 6.42 | 0.875 | 7700 | 4735 | 850 | 110.4799 | 2023-01-16 | 6.205 | 3.975 | 58.16 | 6 | 5.57 | 53.95 | 576 | 650 | 0.88615 | 195 | 2023-01-16 | 6.77 | 5.53 | 48.1 | 1560 | 1900 | 0.82105 | 22.34 | 6.51 | 5.69 | 47.8 | 1044 | 1425 | 0.73263 | 15.98 | 2023-01-16 | 6.65 | 5.71 | 50.49 | 21.91 | 51.79 | 103 | - | - | - | 556 | 141 | 6.89 | 2.77
2023-01-17 | 1.8 | 13.09 | 14.89 | 791.2216 | 18.819 | 7.13 | 433.9 | 892 | 555 | 64 | 65.5 | 7.14 | 494.1 | 1039 | 650 | - | 41000000 | 19000000 | 2023-01-17 | 510 | 7.04 | 365 | 329.1 | 703 | 257 | 6.42 | 27 | 12.7 | 98 | 14130 | 6.71 | 20 | 11.7 | 136 | 15520 | 2023-01-17 | 7.09 | 5.5 | 38 | 8.7 | 8 | 22 | 6.82 | 6 | 63 | 9 | 710 | 200 | 0.5 | 2023-01-17 | 6.725 | 0.755 | 6615 | 4035 | 855 | 130.1273 | 6.795 | 0.555 | 7560 | 4575 | 840 | 111.3779 | 2023-01-17 | 6.22 | 3.95 | 56.425 | 6.12 | 5.5 | 53.61 | 744 | 675 | 1.1022 | 154 | 2023-01-17 | 6.79 | 4.69 | 46.44 | 1488 | 2000 | 0.744 | 22,46 | 6.67 | 5.84 | 50.47 | 1008 | 1350 | 0.74667 | 15,67 | 2023-01-17 | 6.59 | 4.26 | 44.72 | 21.75 | 47.85 | 166 | - | - | - | 453 | 170 | 7.03 | 2.14
2023-01-18 | 1.9 | 13.7 | 15.6 | 775.772 | 20.109 | 7.03 | 559.1 | 895 | 470 | 70 | 75 | 7.29 | 478.9 | 993 | 575 | - | 30000000 | 11000000 | 2023-01-18 | 685 | 7.19 | 1000 | 328.9 | 682 | 271 | 6.79 | 19 | 12.1 | 108 | 12850 | 6.86 | 10 | 9.7 | 161 | 16420 | 2023-01-18 | 7.13 | 7 | 80 | 8 | 15 | 16 | 7.02 | 5.2 | 52 | 8.2 | 610 | Nil | 0.2 | 2023-01-18 | 6.92 | 0.625 | 6470 | 5050 | 895 | 138.3308 | 6.97 | 0.37 | 7480 | 5745 | 905 | 120.9841 | 2023-01-18 | 6.45 | 4.5975 | 51.83 | 6.47 | 5.82 | 54.81 | 696 | 700 | 0.99429 | 173 | 2023-01-18 | 7 | 4.71 | 43.45 | 1704 | 1975 | 0.86278 | 22.56 | 6.7 | 5.32 | 53.48 | 1068 | 1525 | 0.70033 | 15.34 | 2023-01-18 | 7.01 | 3.41 | 49.32 | 21.57 | 49.68 | 157 | - | - | - | 453 | 113 | 6.81 | 3.12
2023-01-19 | 1.8 | 14.64 | 16.44 | 953.541 | 17.241 | 6.78 | 659.4 | 1210 | 775 | 78 | 105 | 7.09 | 779.1 | 1539 | 1080 | - | 44000000 | 23000000 | 2023-01-19 | 625 | 7.22 | 1050 | 599.1 | 1504 | 262 | 6.91 | 25 | 15.1 | 122 | 12280 | 6.84 | 14 | 13.1 | 168 | 14900 | 2023-01-19 | 7.12 | 7.7 | 59 | 8.7 | 8 | 14 | 6.98 | 6.6 | 63 | 8.6 | 810 | Nil | 0.2 | 2023-01-19 | 6.895 | 0.61 | 7085 | 5240 | 895 | 126.3287 | 6.925 | 0.82 | 7160 | 5540 | 885 | 123.6111 | 2023-01-19 | 6.51 | 5.015 | 49.27 | 6.24 | 6.19 | 54.66 | 516 | 800 | 0.645 | 181 | 2023-01-19 | 7 | 5.23 | 43.19 | 1404 | 1850 | 0.75892 | 22.69 | 6.79 | 6.36 | 45.58 | 1152 | 1475 | 0.78102 | 15.01 | 2023-01-19 | 6.8 | 5.27 | 48.88 | 21.31 | 49.31 | 167 | - | - | - | 556 | 141 | 7.09 | 3.22
2023-01-20 | 1.7 | 14.57 | 16.27 | 983.9139 | 16.536 | 6.99 | 599.4 | 1014 | 905 | 84 | 104.5 | 6.95 | 569.4 | 1203 | 600 | - | 58000000 | 44000000 | 2023-01-20 | 485 | 7.02 | 490 | 509.4 | 920 | 282 | 6.49 | 25 | 16.4 | 56 | 11630 | 6.87 | 14 | 12.4 | 52 | 17180 | 2023-01-20 | 7.21 | 6.9 | 38 | 8 | 14 | 8 | 7.09 | 8 | 38 | 9.6 | 770 | 330 | 0.5 | 2023-01-20 | 6.42 | 0.62 | 7325 | 4520 | 845 | 116.0046 | 6.62 | 0.645 | 8200 | 5070 | 830 | 101.3031 | 2023-01-20 | 6.2075 | 4.3825 | 51.595 | 6.19 | 6.05 | 54.6 | 504 | 725 | 0.69517 | 197 | 2023-01-20 | 6.86 | 4.93 | 45.32 | 1392 | 1775 | 0.78423 | 22.71 | 6.76 | 5.9 | 46.36 | 1044 | 1375 | 0.75927 | 14.95 | 2023-01-20 | 6.69 | 5.66 | 46.65 | 21.37 | 47.88 | 173 | - | - | - | 226 | 85 | 6.83 | 2.81
2023-01-21 | 1.9 | 13.91 | 15.81 | 840.0638 | 18.82 | 7.2 | 779.1 | 1067 | 800 | 74 | 85.5 | 7.06 | 359.4 | 1158 | 460 | - | 52000000 | 31000000 | 2023-01-21 | 675 | 7 | 365 | 329.4 | 892 | 245 | 6.68 | 18 | 12.4 | 56 | 9540 | 6.77 | 11 | 10.4 | 70 | 17090 | 2023-01-21 | 7.48 | 6.6 | 73 | 8.7 | 9 | 8 | 7.03 | 7.3 | 63 | 9.8 | 540 | 200 | 0.5 | 2023-01-21 | 6.515 | 0.64 | 6715 | 4600 | 850 | 126.7138 | 6.65 | 0.48 | 8370 | 6005 | 875 | 104.5629 | 2023-01-21 | 6.3675 | 4.315 | 54.2275 | 6.28 | 5.84 | 57.71 | 504 | 825 | 0.61091 | 147 | 2023-01-21 | 6.92 | 5.23 | 42.93 | 1356 | 1725 | 0.78609 | 22.76 | 6.84 | 5.98 | 46.23 | 1056 | 1575 | 0.67048 | 14.9 | 2023-01-21 | 6.72 | 5.64 | 46.57 | 25.6 | 48.28 | 154 | - | - | - | 283 | 56 | 6.73 | 2.06
2023-01-22 | 1.7 | 14.17 | 15.87 | 849.1626 | 18.689 | 7.3 | 719.3 | 1133 | 760 | 100 | 131 | 7.65 | 689.1 | 1126 | 720 | - | 49000000 | 20000000 | 2023-01-22 | 640 | 7.43 | 535 | 599.1 | 972 | 252 | 7.05 | 14 | 14.1 | 101 | 11340 | 7.03 | 18 | 16.1 | 115 | 18090 | 2023-01-22 | 7.19 | 6.1 | 79 | 8 | 9 | 23 | 7.29 | 7 | 66 | 8.6 | 340 | Nil | 0.5 | 2023-01-22 | 6.36 | 0.495 | 6955 | 4120 | 875 | 125.8233 | 6.795 | 0.57 | 7905 | 4860 | 865 | 109.4521 | 2023-01-22 | 6.5325 | 3.9025 | 56.5975 | 6.15 | 5.44 | 55.34 | 588 | 675 | 0.87111 | 180 | 2023-01-22 | 7.02 | 4.51 | 45.76 | 1380 | 1625 | 0.84923 | 22.76 | 6.61 | 5.71 | 49.04 | 1152 | 1475 | 0.78102 | 14.57 | 2023-01-22 | 6.94 | 5.92 | 40.1 | 21.14 | 48.78 | 172 | - | - | - | 283 | 85 | 7.01 | 3.19
2023-01-23 | 1.7 | 14.69 | 16.39 | 903.8769 | 18.133 | 7.22 | 419.3 | 1174 | 450 | 100.8 | 22.4 | 7.72 | 569.3 | 1210 | 660 | - | 30000000 | 16000000 | 2023-01-23 | 795 | 7.12 | 1370 | 539.3 | 966 | 243 | 6.97 | 19 | 14.3 | 100 | 10800 | 6.94 | 19 | 17.3 | 113 | 18837 | 2023-01-23 | 7.23 | 7.9 | 92 | 8.7 | 7.5 | 22.4 | 7 | 6.1 | 84 | 8.4 | 450 | 100 | 0.5 | 2023-01-23 | 6.52 | 0.59 | 6985 | 4515 | 855 | 122.9863 | 6.775 | 0.645 | 8170 | 5275 | 885 | 108.3675 | 2023-01-23 | 6.44 | 4.3575 | 49.7225 | 6.4 | 5.77 | 54.51 | 840 | 700 | 1.2 | 174 | 2023-01-23 | 6.84 | 6.89 | 47.57 | 1764 | 1550 | 1.1381 | 22.88 | 6.81 | 6.52 | 50.82 | 1020 | 1450 | 0.70345 | 14.51 | 2023-01-23 | 6.96 | 6.5 | 45.14 | 22.07 | 49.61 | 169 | - | - | - | 226 | 56 | 6.45 | 2.81
2023-01-24 | 1.7 | 11.58 | 13.28 | 801.0133 | 16.579 | 7.3 | 404.3 | 1076 | 625 | 63.8 | 92.5 | 7.48 | 569.3 | 1190 | 585 | - | 64000000 | 20000000 | 2023-01-24 | 520 | 7.19 | 745 | 569.3 | 1151 | 240 | 6.96 | 26 | 20.3 | 97 | 8500 | 6.94 | 26 | 17.3 | 89 | 15590 | 2023-01-24 | 7.09 | 5 | 84 | 10 | 6.5 | 16.2 | 7.03 | 7.6 | 87 | 9 | 520 | 200 | 0.2 | 2023-01-24 | 6.57 | 0.57 | 6370 | 4060 | 815 | 128.0302 | 6.505 | 0.475 | 8285 | 5420 | 890 | 107.441 | 2023-01-24 | 6.455 | 4.1625 | 55.3475 | 6.4 | 5.81 | 55.81 | - | 700 | - | 175 | 2023-01-24 | 7.06 | 4.95 | 47.52 | 1020 | 1675 | 0.60896 | 22.91 | 6.74 | 5.77 | 49.74 | 828 | 1300 | 0.63692 | 14.51 | 2023-01-24 | 7.31 | 5.3 | 55.16 | 21.18 | 50.83 | 151 | - | - | - | 453 | 113 | 7.03 | 3.01
2023-01-25 | 1.5 | 13.23 | 14.73 | 921.2584 | 15.989 | 6.98 | 659 | 767 | 725 | 74.5 | 47 | 7.18 | 359.3 | 1143 | 680 | - | 47000000 | 14000000 | 2023-01-25 | 575 | 7.11 | 1110 | 344.3 | 978 | 367 | 6.77 | 28 | 7.7 | 120 | 10580 | 6.78 | 14 | 10.7 | 110 | 14750 | 2023-01-25 | 7.12 | 7.6 | 77 | 9.3 | 3.5 | 17.4 | 6.96 | 4.4 | 89 | 9.4 | 480 | 100 | 0.6 | 2023-01-25 | 6.52 | 0.92 | 5850 | 3180 | 705 | 120.7918 | 6.545 | 0.63 | 7675 | 4865 | 875 | 114.0855 | 2023-01-25 | 6.4625 | 3.7775 | 56.0425 | 6.42 | 5.58 | 58.29 | - | 600 | - | 114 | 2023-01-25 | 7 | 4.84 | 50.94 | 1212 | 1675 | 0.72358 | 23.89 | 6.78 | 6.14 | 50.03 | 1056 | 1675 | 0.63045 | 15.08 | 2023-01-25 | 7.28 | 4.73 | 48.39 | 20.82 | 51.4 | 171 | - | - | - | 283 | 56 | 6.79 | 3.11
2023-01-26 | 1.7 | 14.65 | 16.35 | 779.7224 | 20.969 | 6.98 | 449.1 | 1438 | 690 | 89.6 | 91.5 | 7.26 | 569 | 940 | 695 | - | 39000000 | 21000000 | 2023-01-26 | 495 | 7.05 | 700 | 539 | 752 | 243 | 6.81 | 32 | 19 | 110 | 7950 | 6.83 | 19 | 16 | 156 | 14310 | 2023-01-26 | 6.94 | 9.1 | 87 | 13.7 | 4.5 | 12.3 | 6.83 | 7.3 | 84 | 9.4 | 400 | Nil | 0.2 | 2023-01-26 | 6.725 | 1.015 | 5610 | 3710 | 680 | 120.8217 | 6.715 | 0.875 | 7240 | 3660 | 805 | 111.3494 | 2023-01-26 | 6.5175 | 3.9825 | 55.075 | 6.45 | 5.54 | 55.7 | 684 | 550 | 1.2436 | 161 | 2023-01-26 | 7.08 | 4.94 | 44.87 | 1572 | 2125 | 0.73976 | 24.89 | 6.73 | 5.95 | 46.75 | 1092 | 1375 | 0.79418 | 16.01 | 2023-01-26 | 6.94 | 4.71 | 52.44 | 21.68 | 52.19 | 181 | - | - | - | 226 | 85 | 7.02 | 2.89
2023-01-27 | 1.7 | 14.66 | 16.36 | 908.8889 | 18 | 6.99 | 479.2 | 965 | 740 | 89.6 | 59 | 6.98 | 539.1 | 1483 | 685 | - | 33000000 | 17000000 | 2023-01-27 | 670 | 7.1 | 740 | 599.1 | 1364 | 258 | 6.31 | 27 | 23.1 | 91 | 8750 | 6.43 | 35 | 18.1 | 59 | 14600 | 2023-01-27 | 6.91 | 8.2 | 59 | 11.7 | 10.5 | 12.3 | 6.53 | 11.1 | 52 | 15.4 | 340 | 100 | 0.2 | 2023-01-27 | 6.52 | 1.005 | 5830 | 3455 | 550 | 93.5589 | 6.685 | 0.69 | 7105 | 4285 | 665 | 93.6364 | 2023-01-27 | 6.35 | 4.2775 | 54.8925 | 6.54 | 5.64 | 56.51 | 564 | 425 | 1.3271 | 123 | 2023-01-27 | 6.99 | 7.92 | 44.61 | 1404 | 1875 | 0.7488 | 25.67 | 6.73 | 6.73 | 50.88 | 1368 | 1450 | 0.94345 | 17.89 | 2023-01-27 | 6.81 | 4.84 | 59.69 | 22.86 | 57.32 | 165 | - | - | - | 226 | 85 | 6.71 | 3.04
2023-01-28 | 1.7 | 15.51 | 17.21 | 1066.2949 | 16.14 | 7.1 | 539 | 824 | 650 | 62.2 | 75.5 | 7.13 | 479.2 | 1014 | 650 | - | 40000000 | 22000000 | 2023-01-28 | 570 | 7.05 | 980 | 449.2 | 979 | 244 | 6.63 | 27 | 21.2 | 77 | 7930 | 6.69 | 28 | 17.2 | 112 | 12320 | 2023-01-28 | 6.94 | 7 | 97 | 9 | 9 | 12.9 | 6.85 | 8.2 | 91 | 11 | 250 | 100 | 0.2 | 2023-01-28 | 6.635 | 0.965 | 5600 | 3125 | 675 | 123.5424 | 6.525 | 0.57 | 6555 | 3810 | 705 | 107.4293 | 2023-01-28 | 6.465 | 4.555 | 43.2725 | 6.8 | 5.82 | 51.83 | 924 | 575 | 1.607 | 145 | 2023-01-28 | 6.98 | 4.44 | 47.01 | 1284 | 1800 | 0.71333 | 26.12 | 6.73 | 6.45 | 44.35 | 1512 | 1325 | 1.1411 | 18.76 | 2023-01-28 | 6.91 | 4.68 | 53.32 | 21.45 | 57.55 | 176 | - | - | - | 453 | 56 | 6.59 | 2.74
2023-01-29 | 1.7 | 11.9 | 13.6 | 810.6819 | 16.776 | 6.94 | 419.3 | 680 | 510 | 64.4 | 76.5 | 7.02 | 449 | 718 | 480 | - | 37000000 | 11000000 | 2023-01-29 | 400 | 6.94 | 783 | 569 | 905 | 222 | 6.74 | 26 | 22 | 169 | 8510 | 6.68 | 26 | 20 | 126 | 14130 | 2023-01-29 | 6.94 | 7.3 | 48 | 8 | 8.5 | 17.9 | 6.92 | 8 | 87 | 8.2 | 300 | Nil | 0.5 | 2023-01-29 | 6.715 | 0.965 | 5890 | 3725 | 720 | 121.075 | 6.61 | 0.8 | 6720 | 4330 | 760 | 112.8489 | 2023-01-29 | 6.2925 | 3.875 | 59.525 | 6.42 | 4.92 | 58.55 | 900 | 775 | 1.1613 | 138 | 2023-01-29 | 6.94 | 4.76 | 47.38 | 1188 | 1650 | 0.72 | 26.12 | 6.61 | 5.53 | 50.8 | 1140 | 1375 | 0.82909 | 19.21 | 2023-01-29 | 6.76 | 4.9 | 49.88 | 20.76 | 50.23 | 161 | - | - | - | 340 | 226 | 6.39 | 2.81
2023-01-30 | 1.2 | 12.37 | 13.57 | 750.5531 | 18.08 | 7.05 | 509 | 967 | 530 | 65 | 44.5 | 6.96 | 509.3 | 1025 | 620 | - | 24000000 | 17000000 | 2023-01-30 | 595 | 6.94 | 1063 | 659.3 | 1150 | 254 | 6.8 | 32 | 17.3 | 41 | 10340 | 6.77 | 16 | 14.3 | 64 | 14250 | 2023-01-30 | 6.98 | 8 | 98 | 8.7 | 8 | 8.4 | 6.96 | 7.3 | 71 | 7.6 | 400 | 100 | 0.2 | 2023-01-30 | 6.52 | 1.015 | 5685 | 3820 | 765 | 134.2871 | 6.6 | 0.865 | 6450 | 4420 | 805 | 124.7596 | 2023-01-30 | 6.3375 | 4.6825 | 46.88 | 6.27 | 5.53 | 53.05 | 672 | 925 | 0.72649 | 145 | 2023-01-30 | 6.89 | 5.89 | 41.92 | 1116 | 1550 | 0.72 | 26.33 | 6.53 | 6.21 | 47.73 | 1025 | 1125 | 0.91111 | 18.34 | 2023-01-30 | 6.77 | 4.89 | 51.4 | 21.07 | 50.56 | 169 | - | - | - | 283 | 56 | 7.02 | 3.04
2023-01-31 | 2.1 | 6.45 | 8.55 | 836.0223 | 10.227 | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-01-31 | - | - | - | - | - | 212 | - | - | - | - | - | - | - | - | - | - | 2023-01-31 | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-01-31 | 6.465 | 4.825 | 5750 | 4265 | 755 | 131.1441 | 6.475 | 3.395 | 6525 | 4270 | 715 | 109.5694 | 2023-01-31 | - | - | - | - | - | - | - | - | - | 141 | 2023-01-31 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-01-31 | - | - | - | - | - | 42 | - | - | - | - | - | - | -
AVG | 1.5774 | 13.1632 | 14.7406 | 839.9246 | 17.6347 | 7.062 | 503.8 | 906.2333 | 613.3333 | 76.2167 | 74.63 | 7.169 | 528.1333 | 979.4333 | 653.3333 |  | 42466666.6667 | 19533333.3333 | AVG | 578.6667 | 7.0863 | 866.2 | 444.1333 | 750.1 | 276.8387 | 6.76 | 22.4 | 15.2667 | 85.9 | 9929 | 6.8143 | 20.8667 | 14.6267 | 94.4667 | 14075.5667 | AVG | 7.1447 | 7.29 | 63.1667 | 9.6457 | 8.4833 | 17.1333 | 6.966 | 7.3533 | 62.4 | 10.03 | 590.3571 | 215.9091 | 0.34333 | AVG | 6.7056 | 0.98355 | 6272.0968 | 3965.4839 | 781.2903 | 124.6286 | 6.7321 | 0.89677 | 7198.871 | 4583.2258 | 821.7742 | 114.5589 | AVG | 6.4331 | 4.2366 | 53.7266 | 6.369 | 5.486 | 54.434 | 714.8571 | 580 | 1.3517 | 167.2258 | AVG | 6.9173 | 5.2413 | 45.729 | 1293.2 | 1680 | 0.77546 | 23.239 | 6.7353 | 5.8297 | 46.7097 | 1134.9667 | 1472.5 | 0.77878 | 16.7448 | AVG | 6.8362 | 4.9768 | 47.5836 | 21.8811 | 50.1975 | 159.9032 |  |  |  | 432.9667 | 122.4 | 6.8177 | 2.979
Remarks: Analysis not done in 31st January Plant shut down (Due to CCT tank and Plant water sump cleaning) | [18 empty] | Remarks: | [30 empty] | Remarks: | [12 empty] | Remarks: | [10 empty] | Remarks: | [14 empty] | Remarks:
*BDL - Below Detectable Limit, ([-] - analysis not conducted) | [18 empty] | *BDL - Below Detectable Limit | [16 empty] | *BDL - Below Detectable Limit | [13 empty] | *BDL - Below Detectable Limit | [12 empty] | *BDL - Below Detectable Limit | [10 empty] | *BDL - Below Detectable Limit | [14 empty] | *BDL - Below Detectable Limit
VA TECH WABAG | [14 empty] | PID | KVWSMB |  |  | VA TECH WABAG | [7 empty] | PID |  |  |  |  | KVWSMB |  |  |  | VA TECH WABAG | [9 empty] | PID | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  | KVWSMB |  |  |  | VA TECH WABAG |  |  |  |  | PID |  |  | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  |  | KVWSMB |  |  |  |  | VA TECH WABAG | [9 empty] | PID |  | KVWSMB
CHEMIST |  |  |  |  | PLANT INCHARGE | [6 empty] | PLANT INCHARGE | [6 empty] | CHEMIST |  | PLANT INCHARGE | [14 empty] | CHEMIST | [7 empty] | PLANT INCHARGE | [5 empty] | CHEMIST |  | PLANT INCHARGE | [10 empty] | CHEMIST |  | PLANT INCHARGE | [8 empty] | CHEMIST |  | PLANT INCHARGE | [12 empty] | CHEMIST |  |  | PLANT INCHARGE
Formulas:
Date = [Date]
Aeration Tank = [Date]
Digester Sludge Feeding Details = [Aeration Tank]
Digester Performance Details = [Digester Sludge Feeding Details]
Digester Outlet = [Digester Performance Details]