## Lab Report - JUNE 2023
s | [18 empty] | s | [16 empty] | s | [13 empty] | s | [12 empty] | s | [10 empty] | s | [14 empty] | s
KATHMANDU, NEPAL | [18 empty] | KATHMANDU, NEPAL | [16 empty] | KATHMANDU, NEPAL | [13 empty] | KATHMANDU, NEPAL | [12 empty] | KATHMANDU, NEPAL | [10 empty] | KATHMANDU, NEPAL | [14 empty] | KATHMANDU, NEPAL
Project No: | 10M170 | [13 empty] | Month: | 2023-06-01 |  |  | Project No: | 10M170 | [10 empty] | Month: |  |  | 2023-06-01 |  | Project No: | 10M170 | [8 empty] | Month: | 2023-06-01 |  |  | Project No: |  | 10M170 | [6 empty] | Month: | 2023-06-01 |  |  | Project No: | 10M170 | [6 empty] | Month: | 2023-06-01 |  | Project No: |  | 10M170 | [7 empty] | Month: | 2023-06-01 |  |  |  | Project No: | 10M170 | [9 empty] | Month: | 2023-06-01
Date | Power Generation and Consumption |  |  |  | Inlet | [13 empty] | Date | Grit Classifier Outlet | Primary Clarifier |  |  |  |  | Secondary Clarifier |  |  |  |  | Secondary Sedimentation tank Outlet |  |  |  |  | Date | CHLORINE CONTACT TANK (Composite) | [5 empty] | CHLORINE CONTACT TANK | [6 empty] | Aeration Tank | [12 empty] | Digester Sludge Feeding Details | [10 empty] | Digester Performance Details | [14 empty] | Digester Outlet |  |  |  | Centrifuge |  |  | Bio Gas |  |  | Scrubber |  | Odour Control Unit
| Power Generation from Gas Engine | Daily Power Consumption from NEA (MW) | Total Power Consumption from NEA & GE (MW) | Total Power (KWh)/Flow (ML) | Raw Sewage Flow | Raw Sewage (Composite) | [5 empty] | Raw Sewage | [37 empty] | DATE | Existing Aeration Tank | [5 empty] | New Aeration Tank | [5 empty] | DATE | Primary sedimentation tank Underflow |  |  | Thickener Sludge Parameters | [6 empty] | DATE | Digester - A | [6 empty] | Digester - B | [6 empty] | DATE | Centrifuge Feed |  |  | Centrifuge Cake |  | Centrifuge Feed Totalizer | Gas Generation |  |  | Inlet | Outlet
[6 empty] | pH | BOD5 | COD | TSS | NH3-N | O & G | pH | BOD5 | COD | TSS | TP | Total Coliform | Fecal coliform |  | TSS | PH | TSS | BOD5 | COD | PST Sludge Totalizer | PH | TSS | BOD5 | COD | Existing RAS | PH | TSS | BOD5 | COD | New RAS |  | pH | BOD5 | COD | TSS | O & G | Ammonical Nitrogen | pH | BOD5 | COD | TSS | Total Coliform | Fecal coliform | FRC |  | PH | DO | MLSS | MLVSS | SV30 | SVI | PH | DO | MLSS | MLVSS | SV30 | SVI |  | pH | TS | VS | pH | TS | VS | VFA | Alkalinity | VFA/ Alkalinity Ratio | Digester Feed Totalizer |  | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp | pH | TS | VS | VFA - mg/l | Alkalinity | VFA/ Alkalinity Ratio | Temp |  | PH | TS | VS | TS | VS |  |  |  |  | H2S | H2S | Inlet pH | Outlet pH
Control Limits |  |  |  |  | 32.4 | 6.0 - 9.0 | 300 | 800 | 400 | 79 | 120 | 6.0 - 9.0 | 300 | 800 | 400 | 12 | 107-109 | 106-107 | Control Limits | - | [15 empty] | Control Limits | 6.5-8.0 | < 10 | < 250 | < 10 | < 10 | < 50 | 6.5-8.0 | < 10 | < 250 | < 10 | < 500 | < 100 | Max 1 | Control Limits | - | > 0.5 | - | - | - | - | - | > 0.5 | - | - | - | - | Control Limits | [10 empty] | Control Limits | [14 empty] | Control Limits | [7 empty] | CH4 | CO2
Units | MW | <482.02 KWh / ML of Treated Water |  |  | MLD | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Units | mg/L | - | mg/L | mg/L | mg/L | m3 | - | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | mg/L | Units | - | mg/L | mg/L | mg/L | mg/L | mg/L | - | mg/L | mg/L | mg/L | MPN /100ml | MPN /100ml | mg/L | Units | - | mg/L | mg/L | mg/L | ml/L | - | - | mg/L | mg/L | mg/L | ml/L | - | Units | - | % | % | - | % | % | mg/l | mg/l | - | m3 | Units | - | % | % | mg/l | mg/l | - | 0C | - | % | % | mg/l | mg/l | - | 0C | Units | - | % | % | % | % | m3 | Nm3 |  |  | ppm | ppm | - | -
2023-06-01 | 1 | 9.99 | 10.99 | 661.8887 | 16.604 | 7.18 | 344.6 | 914 | 375 | 67.8 | 58 | 7.21 | 389.1 | 1038 | 405 | 5.21 | 46000000 | 21000000 | 2023-06-01 | 365 | 7.11 | 1135 | 554.1 | 1164 | 405 | 7.21 | 17 | 15.3 | 58 | 10550 | 7.19 | 29 | 16.5 | 66 | 5070 | 2023-06-01 | 7.29 | 18.2 | 58 | 22.5 | 4.5 | 10.6 | 7.4 | 13.5 | 81 | 15.5 | 480 | 90 | 0.1 | 2023-06-01 | 6.795 | 0.545 | 6100 | 4410 | 920 | 150.9009 | 6.595 | 0.375 | 4570 | 2730 | 795 | 174.4712 | 2023-06-01 | 6.585 | 2.54 | 55.945 | 6.37 | 3.75 | 52.22 | 840 | 525 | 1.6 | 200 | 2023-06-01 | 6.71 | 3.24 | 50.97 | 1884 | 1450 | 1.2993 | 28 | 6.66 | 3.92 | 50.12 | 2280 | 1375 | 1.6582 | 28 | 2023-06-01 | 7.13 | 2.97 | 49.76 | 21.18 | 54.38 | 170 | - |  |  | 566 | 113 | - | -
2023-06-02 | 1.8 | 7.79 | 9.59 | 521.6493 | 18.384 | 7.08 | 419.3 | 1063 | 455 | 80.6 | 75.5 | 7.09 | 374.6 | 968 | 475 | 11.14 | 32000000 | 19000000 | 2023-06-02 | 505 | 7.1 | 765 | 479.6 | 1124 | 393 | 7.04 | 14 | 12.2 | 50 | 9570 | 7.09 | 15 | 13.4 | 48 | 9980 | 2023-06-02 | 7.3 | 19.1 | 58 | 24 | 8 | 28 | 7.36 | 11.6 | 52 | 12 | 550 | 170 | 0.2 | 2023-06-02 | 6.81 | 0.295 | 7005 | 4100 | 945 | 135.5306 | 6.685 | 0.24 | 5610 | 3525 | 800 | 142.7818 | 2023-06-02 | 6.61 | 3.32 | 51.3325 | 6.4 | 3.83 | 54.47 | 1002 | 375 | 2.672 | 189 | 2023-06-02 | 7.14 | 3.63 | 50.27 | 1770 | 1500 | 1.18 | 28 | 6.95 | 3.1 | 45.9 | 2046 | 1350 | 1.5156 | 28 | 2023-06-02 | 6.9 | 3.13 | 47.06 | 21.77 | 52.05 | 161 | - |  |  | 566 | 113 | - | -
2023-06-03 | 1.1 | 10.19 | 11.29 | 553.106 | 20.412 | 7 | 419.5 | 1158 | 460 | 57.1 | 76.5 | 6.98 | 464.3 | 1102 | 565 | 8.204 | 50000000 | 21000000 | 2023-06-03 | 520 | 6.97 | 1030 | 539.3 | 1145 | 348 | 7.04 | 19 | 16.7 | 79 | 9740 | 7 | 20 | 17.3 | 77 | 10860 | 2023-06-03 | 7.75 | 15.1 | 42 | 15.5 | 5.5 | 13.7 | 7.11 | 14.9 | 66 | 18 | 590 | 120 | 0.2 | 2023-06-03 | 6.825 | 0.685 | 6475 | 4410 | 940 | 145.5492 | 6.755 | 0.285 | 6035 | 4040 | 900 | 149.4061 | 2023-06-03 | 6.6225 | 3.32 | 53.2575 | 6.44 | 3.3 | 50.64 | 840 | 350 | 2.4 | 170 | 2023-06-03 | 7.14 | 4.26 | 50.12 | 1734 | 1500 | 1.156 | 28 | 6.91 | 4.71 | 50.02 | 2004 | 1275 | 1.5718 | 28 | 2023-06-03 | 6.88 | 2.95 | 48.35 | 22.89 | 55.39 | 170 | - |  |  | - | - | - | -
2023-06-04 | 1.5 | 9.56 | 11.06 | 646.3301 | 17.112 | 7.44 | 418.9 | 1112 | 445 | 78.4 | 69 | 7.21 | 494.5 | 1204 | 530 | 5.228 | 49000000 | 36000000 | 2023-06-04 | 545 | 7.13 | 895 | 524.5 | 1170 | 338 | 7.4 | 13 | 12.7 | 34 | 10860 | 7.38 | 27 | 19.3 | 40 | 9820 | 2023-06-04 | 7.78 | 12.1 | 68 | 16 | 8 | 12.3 | 7.48 | 16.9 | 36 | 18.5 | 510 | 160 | 0.2 | 2023-06-04 | 6.82 | 0.56 | 6310 | 2905 | 935 | 148.846 | 6.68 | 0.35 | 6100 | 3125 | 880 | 144.3978 | 2023-06-04 | 6.8375 | 3.2575 | 59.1475 | 6.71 | 3.21 | 56.74 | 750 | 400 | 1.875 | 170 | 2023-06-04 | 7.09 | 3.84 | 51.66 | 1704 | 1550 | 1.0994 | 28 | 7.12 | 3.58 | 50.95 | 1866 | 1400 | 1.3329 | 28 | 2023-06-04 | 7 | 3.4691 | 50.8857 | 20.42 | 50.79 | 167 | - |  |  | 566 | 170 | - | -
2023-06-05 | 1.1 | 10.17 | 11.27 | 646.5493 | 17.431 | 7.35 | 418.9 | 1064 | 430 | 57.7 | 60.5 | 7.4 | 508.9 | 1204 | 670 | 7.36 | 56000000 | 27000000 | 2023-06-05 | 725 | 7.38 | 1745 | 418.9 | 1266 | 365 | 7.56 | 17 | 15.1 | 60 | 10080 | 7.62 | 33 | 19.3 | 64 | 9470 | 2023-06-05 | 7.6 | 9.4 | 98 | 22 | 4.5 | 14.3 | 7.75 | 12.7 | 68 | 19.8 | 590 | 210 | 0.5 | 2023-06-05 | 7.37 | 0.295 | 6250 | 3795 | 890 | 143.835 | 7.39 | 0.265 | 5870 | 3760 | 820 | 139.9944 | 2023-06-05 | 7.01 | 2.94 | 56.2075 | 7.13 | 3.62 | 53.4 | 852 | 425 | 2.0047 | 132 | 2023-06-05 | 7.39 | 3.15 | 50.8 | 1860 | 1525 | 1.2197 | 28 | 7.41 | 3.86 | 49.2 | 1644 | 1450 | 1.1338 | 28 | 2023-06-05 | 7.38 | 3.0343 | 49.2386 | 19.89 | 52.77 | 170 | - |  |  | 340 | 170 | - | -
2023-06-06 | 1.5 | 10.95 | 12.45 | 694.832 | 17.918 | 6.92 | 374.4 | 1002 | 480 | 69.4 | 76 | 7.2 | 313.9 | 1157 | 345 | 6.202 | 32000000 | 16000000 | 2023-06-06 | 830 | 7.19 | 830 | 493.9 | 1028 | 386 | 7.25 | 11 | 9.1 | 62 | 9880 | 7.12 | 25 | 15.7 | 111 | 8370 | 2023-06-06 | 6.88 | 12.2 | 90 | 17.3 | 7.5 | 18.2 | 7.17 | 9.4 | 87 | 18 | 630 | 200 | 0.2 | 2023-06-06 | 7.115 | 0.67 | 6185 | 3910 | 910 | 148.0984 | 7.085 | 0.305 | 7410 | 4800 | 895 | 121.1699 | 2023-06-06 | 6.9375 | 2.785 | 63.25 | 7.11 | 3.76 | 57.72 | 786 | 375 | 2.096 | 181 | 2023-06-06 | 7.28 | 3.26 | 53.67 | 1788 | 1625 | 1.1003 | 28 | 7.33 | 3.16 | 53.18 | 1920 | 1475 | 1.3017 | 28 | 2023-06-06 | 7.31 | 3.4219 | 52.7559 | 21.7 | 57.31 | 175 | - |  |  | 566 | 296 | - | -
2023-06-07 | 1.2 | 10.9 | 12.1 | 720.3238 | 16.798 | 7.2 | 449.6 | 1080 | 490 | 47 | 70 | 6.87 | 419.4 | 1036 | 540 | 9.026 | 41000000 | 38000000 | 2023-06-07 | 860 | 6.84 | 705 | 524.4 | 985 | 348 | 6.82 | 17 | 15.6 | 72 | 10150 | 6.78 | 21 | 19.2 | 98 | 11620 | 2023-06-07 | 7.16 | 13.1 | 57 | 19 | 9.5 | 16 | 6.83 | 13.2 | 84 | 19.4 | 610 | 180 | 0.2 | 2023-06-07 | 6.855 | 0.325 | 6815 | 4200 | 915 | 134.6491 | 6.695 | 0.175 | 7160 | 4810 | 940 | 131.3169 | 2023-06-07 | 6.6775 | 2.8375 | 57.4675 | 6.66 | 4.22 | 53.17 | 792 | 325 | 2.4369 | 160 | 2023-06-07 | 6.95 | 3.16 | 53.43 | 1704 | 1525 | 1.1174 | 28 | 6.89 | 3.83 | 50.24 | 1800 | 1475 | 1.2203 | 28 | 2023-06-07 | 6.82 | 3.3156 | 51.1022 | 21.91 | 51.59 | 175 | - |  |  | 566 | 170 | - | -
2023-06-08 | 1.6 | 9.72 | 11.32 | 662.3757 | 17.09 | 7.02 | 524.1 | 823 | 595 | 72.8 | 62 | 7.06 | 509.6 | 1204 | 610 | 10.38 | 51000000 | 20000000 | 2023-06-08 | 450 | 6.98 | 700 | 599.6 | 1136 | 345 | 6.85 | 15 | 14 | 52 | 10130 | 6.8 | 54 | 21.2 | 121 | 12160 | 2023-06-08 | 7.14 | 14.9 | 59 | 21.3 | 6.5 | 19.6 | 7.02 | 15.7 | 58 | 21.7 | 600 | 250 | 0.2 | 2023-06-08 | 6.845 | 0.445 | 6420 | 4255 | 945 | 147.3284 | 6.77 | 0.165 | 7400 | 5100 | 940 | 127.038 | 2023-06-08 | 6.695 | 3.815 | 57.3125 | 6.71 | 3.73 | 55.97 | 660 | 325 | 2.0308 | 174 | 2023-06-08 | 7.12 | 3.43 | 50.87 | 1704 | 1425 | 1.1958 | 28 | 6.98 | 3.55 | 46.29 | 1800 | 1550 | 1.1613 | 28 | 2023-06-08 | 6.94 | 4.1303 | 45.9397 | 22.7 | 52.19 | 171 | - |  |  | 453 | 113 | - | -
2023-06-09 | 1.2 | 12.5 | 13.7 | 756.8643 | 18.101 | 7.15 | 254.4 | 814 | 290 | 53.2 | 52 | 6.94 | 599.1 | 951 | 675 | 11.2 | 30000000 | 19000000 | 2023-06-09 | - | 6.88 | 1100 | 629.1 | 977 | 884 | 6.84 | 46 | 19.5 | 62 | 11410 | 6.68 | 50 | 22.5 | 149 | 13250 | 2023-06-09 | 7.24 | 12.9 | 42 | 15.3 | 7 | 18.5 | 6.88 | 16 | 64 | 31 | 480 | 200 | 0.2 | 2023-06-09 | 6.785 | 0.15 | 6780 | 4660 | 950 | 140.2817 | 6.705 | 0.225 | 7495 | 5085 | 930 | 124.0837 | 2023-06-09 | 6.6475 | 3.0125 | 55.2075 | 6.68 | 3.85 | 56.19 | - | 300 | - | 170 | 2023-06-09 | 7 | 3.54 | 50.01 | 1620 | 1425 | 1.1368 | 29 | 6.91 | 3.44 | 49.18 | 1860 | 1450 | 1.2828 | 29 | 2023-06-09 | 6.82 | 1.7748 | 47.2222 | 24.47 | 41.27 | 179 | - |  |  | 340 | 170 | - | -
2023-06-10 | 1.5 | 10.51 | 12.01 | 731.7816 | 16.412 | 7.21 | 434.2 | 1088 | 485 | 58.2 | 40.5 | 7.06 | 509.4 | 1030 | 560 | 7.01 | 20000000 | 3000000 | 2023-06-10 | - | 6.98 | 660 | 584.4 | 864 | 273 | 6.81 | 16 | 15 | 48 | 11260 | 6.7 | 29 | 23.4 | 104 | 12020 | 2023-06-10 | 7.11 | 14.2 | 66 | 24.3 | 4.5 | 12.9 | 6.96 | 11.4 | 36 | 13 | 500 | 200 | 0.2 | 2023-06-10 | 6.795 | 0.195 | 7125 | 3895 | 955 | 134.3517 | 6.715 | 0.27 | 7925 | 4105 | 950 | 120.1517 | 2023-06-10 | 6.6825 | 3.0675 | 60.94 | 6.64 | 4.25 | 59.82 | 500 | 936 | 0.53419 | 145 | 2023-06-10 | 7.05 | 3.53 | 49.87 | 1806 | 1350 | 1.3378 | 29 | 6.96 | 3.75 | 51.08 | 1518 | 1525 | 0.99541 | 29 | 2023-06-10 | 6.92 | 3.7559 | 50.2304 | 20.57 | 53.5 | 147 | - |  |  | 453 | 113 | - | -
2023-06-11 | 0.9 | 6.41 | 7.31 | 675.2887 | 10.825 | 6.98 | 614.5 | 1304 | 740 | 58.2 | 95 | 6.94 | 509.2 | 1123 | 525 | 7.202 | 35000000 | 26000000 | 2023-06-11 | 320 | 6.92 | 355 | 329.2 | 984 | 159 | 6.71 | 23 | 19.6 | 68 | 13670 | 6.68 | 42 | 24.4 | 84 | 15450 | 2023-06-11 | 7.14 | 13.8 | 48 | 22 | 9 | 18.5 | 6.84 | 13.1 | 52 | 23 | 490 | 120 | 0.5 | 2023-06-11 | 6.745 | 0.16 | 7545 | - | 950 | 126.4122 | 6.7 | 0.21 | 8075 | - | 950 | 117.937 | 2023-06-11 | 6.6275 | 3.11 | 52.825 | 6.6 | 4.74 | 56.48 | 660 | 275 | 2.4 | 115 | 2023-06-11 | 7.01 | 3.37 | 53.55 | 1704 | 1425 | 1.1958 | 29 | 6.96 | 3.72 | 53.81 | 1452 | 1550 | 0.93677 | 29 | 2023-06-11 | 6.9 | 1.82 | 47.86 | 25.47 | 49.8 | 103 | - |  |  | 566 | 296 | - | -
2023-06-12 | 2 | 8.53 | 10.53 | 802.5303 | 13.121 | 6.94 | 254.5 | 865 | 285 | 54.9 | 40.5 | 7.04 | 269.5 | 954 | 300 | 6.308 | 32000000 | 21000000 | 2023-06-12 | 385 | 7.01 | 980 | 644.5 | 1021 | 259 | 6.77 | 13 | 12.1 | 62 | 10720 | 6.79 | 32 | 23.5 | 81 | 13130 | 2023-06-12 | 7.16 | 11.9 | 44 | 15.7 | 6.5 | 15.7 | 6.89 | 11.9 | 50 | 14.7 | 560 | 180 | 0.2 | 2023-06-12 | 6.75 | 0.195 | 7950 | 5105 | 960 | 120.971 | 6.705 | 0.43 | 7870 | 5168 | 955 | 121.5104 | 2023-06-12 | 6.52 | 3.505 | 52.9475 | 6.44 | 4.19 | 57.8 | 744 | 300 | 2.48 | 188 | 2023-06-12 | 6.96 | 3.57 | 52.6 | 1614 | 1350 | 1.1956 | 29 | 6.96 | 3.13 | 55.86 | 1680 | 1450 | 1.1586 | 29 | 2023-06-12 | 7.24 | 2.62 | 52.71 | 26.9 | 55.79 | 165 | - |  |  | 453 | 170 | - | -
2023-06-13 | 0.5 | 8.05 | 8.55 | 720.6676 | 11.864 | 7.16 | 299.1 | 896 | 315 | 65.5 | 40 | 7.01 | 224.5 | 944 | 295 | 7.964 | 29000000 | 17000000 | 2023-06-13 | - | - | - | - | - | 240 | - | - | - | - | - | - | - | - | - | - | 2023-06-13 | 7.34 | 9.6 | 32 | 14.3 | 8.5 | 19.9 | 7.03 | 10.8 | 48 | 13.7 | 420 | 130 | 0.2 | 2023-06-13 | - | - | - | - | - | - | - | - | - | - | - | - | 2023-06-13 | - | - | - | - | - | - | - | - | - | 170 | 2023-06-13 | - | - | - | - | - | - | 29 | - | - | - | - | - | - | 29 | 2023-06-13 | - | - | - | - | - | 144 | - |  |  | 340 | 170 | - | -
2023-06-14 | 2.2 | 6.53 | 8.73 | 634.7244 | 13.754 | 7.09 | 284 | 802 | 230 | 67.8 | 57.5 | 7.24 | 254.1 | 824 | 270 | 8.768 | 36000000 | 20000000 | 2023-06-14 | 210 | 7.21 | 675 | 329.1 | 798 | 374 | 7.05 | 17 | 12.3 | 40 | 10000 | 7.12 | 14 | 12.9 | 34 | 14380 | 2023-06-14 | 7.19 | 8 | 40 | 13 | 7.5 | 11.5 | 7.29 | 9.2 | 36 | 13 | 400 | 150 | 0.2 | 2023-06-14 | 6.935 | 0.885 | 7640 | 4770 | 945 | 124.407 | 6.915 | 0.8 | 6685 | 4355 | 965 | 145.6366 | 2023-06-14 | 6.695 | 3.6825 | 51.875 | 6.8 | 3.26 | 55.82 | 618 | 525 | 1.1771 | 79 | 2023-06-14 | 7.16 | 3.55 | 48.01 | 1146 | 1450 | 0.79034 | 29 | 7.08 | 3.42 | 50.24 | 1002 | 1400 | 0.71571 | 29 | 2023-06-14 | 7.05 | 2.85 | 53.2 | 19.18 | 52.43 | 124 | - |  |  | 566 | 296 | - | -
2023-06-15 | 0.9 | 10.07 | 10.97 | 610.2921 | 15.188 | 7.02 | 179.1 | 654 | 185 | 63.3 | 51.5 | 7.03 | 284 | 864 | 260 | 9.532 | 23000000 | 16000000 | 2023-06-15 | 170 | 7 | 755 | 374 | 910 | 405 | 6.93 | 12 | 10.4 | 54 | 10710 | 6.86 | 13 | 11.6 | 60 | 13120 | 2023-06-15 | 7.26 | 10.4 | 34 | 11.3 | 4.5 | 21.8 | 6.83 | 8 | 40 | 11.3 | 430 | 190 | 0.2 | 2023-06-15 | 6.765 | 1.075 | 7215 | 4505 | 935 | 130.2302 | 6.7 | 2.045 | 6435 | 3715 | 930 | 145.4702 | 2023-06-15 | 6.59 | 3.505 | 54.505 | 6.62 | 2.76 | 52.81 | 594 | 450 | 1.32 | 0 | 2023-06-15 | 6.97 | 3.64 | 49.06 | 1350 | 1425 | 0.94737 | 29 | 6.84 | 4.02 | 50.02 | 1170 | 1375 | 0.85091 | 29 | 2023-06-15 | 6.9 | 3.15 | 51.16 | 22.85 | 59.04 | 123 | - |  |  | 453 | 113 | - | -
2023-06-16 | 0.9 | 12.9 | 13.8 | 764.7548 | 17.975 | 7.12 | 239.4 | 769 | 295 | 63.8 | 54.5 | 7.11 | 299.1 | 880 | 310 | 6.028 | 39000000 | 26000000 | 2023-06-16 | 200 | 7.01 | 1855 | 494.1 | 1124 | 528 | 6.96 | 11 | 10.5 | 40 | 10420 | 7.01 | 13 | 11.7 | 36 | 12110 | 2023-06-16 | 7.3 | 12.2 | 32 | 12.7 | 6 | 21 | 7.19 | 8.5 | 32 | 9 | 500 | 180 | 0.2 | 2023-06-16 | 6.9 | 0.845 | 6475 | 3950 | 940 | 146.3886 | 6.805 | 0.98 | 6430 | 3585 | 925 | 143.8994 | 2023-06-16 | 6.9075 | 3.3175 | 57.6325 | 6.9 | 2.44 | 52.63 | - | 450 | - | 0 | 2023-06-16 | 7.06 | 3.83 | 54.45 | 1194 | 1525 | 0.78295 | 29 | 7.06 | 3.72 | 55.27 | 1236 | 1375 | 0.89891 | 29 | 2023-06-16 | 7.09 | 3.18 | 48.63 | 22.15 | 45.62 | 163 | - |  |  | 566 | 296 | - | -
2023-06-17 | 0.6 | 10.64 | 11.24 | 622.8872 | 18.045 | - | 329.5 | 832 | 355 | 47 | 66 | 7.09 | 284.4 | 814 | 305 | 7.09 | 41000000 | 30000000 | 2023-06-17 | 250 | 7.1 | 970 | 464.4 | 1002 | 183 | 7.1 | 13 | 12 | 50 | 10010 | 7.03 | 18 | 15.6 | 46 | 11820 | 2023-06-17 | - | 9.6 | 40 | 10.7 | 6.5 | 14 | 7.19 | 9.9 | 36 | 11.7 | 530 | 160 | 0.2 | 2023-06-17 | 6.88 | 0.7 | 6395 | - | 940 | 147.6958 | 6.815 | 0.75 | 6205 | - | 910 | 146.696 | 2023-06-17 | 6.7025 | 3.3575 | 52.1025 | 6.8 | 2.41 | 57.04 | 672 | 400 | 1.68 | 0 | 2023-06-17 | 7.02 | 3.55 | 52.8 | 1284 | 1525 | 0.84197 | 29 | 6.92 | 3.72 | 52.61 | 1014 | 1400 | 0.72429 | 29 | 2023-06-17 | 6.91 | 3.36 | 52.12 | 22.11 | 46.71 | 160 | - |  |  | 340 | 170 | - | -
2023-06-18 | 0.8 | 12.99 | 13.79 | 761.5419 | 18.108 | - | 284.1 | 822 | 310 | 52.6 | 32 | - | 284.5 | 844 | 300 | 8.476 | 32000000 | 27000000 | 2023-06-18 | 315 | - | 1330 | 509.5 | 1048 | 417 | - | 15 | 13.9 | 50 | 11370 | - | 14 | 13.3 | 54 | 15560 | 2023-06-18 | - | 8.5 | 45 | 12.7 | 6 | 12.9 | - | 10.4 | 44 | 12.2 | 410 | 80 | 0.2 | 2023-06-18 | - | 0.565 | 8090 | 5170 | 965 | 119.6032 | - | 0.48 | 8265 | 5200 | 955 | 115.5467 | 2023-06-18 | - | 3.1675 | 60.095 | - | 2.35 | 55.66 | 600 | 350 | 1.7143 | 0 | 2023-06-18 | - | 3.9 | 51.15 | 1464 | 1450 | 1.0097 | 29 | - | 3.92 | 52.57 | 1500 | 1350 | 1.1111 | 29 | 2023-06-18 | - | - | - | - | - | 31 | - |  |  | 453 | 170 | - | -
2023-06-19 | 0.8 | 12.51 | 13.31 | 804.0353 | 16.554 | 6.94 | 314 | 840 | 320 | 48.7 | 20 | - | 269.1 | 814 | 285 | 8.374 | 50000000 | 30000000 | 2023-06-19 | 265 | - | 1440 | 449.1 | 964 | 393 | - | 18 | 11.7 | 50 | 11830 | - | 14 | 11.7 | 60 | 14250 | 2023-06-19 | 7.11 | 9.5 | 50 | 17.7 | 4 | 16.2 | - | 7.7 | 48 | 11 | 620 | 200 | 0.2 | 2023-06-19 | - | 0.5 | 7400 | 4945 | 970 | 131.6583 | - | 0.545 | 6930 | 4630 | 950 | 137.4986 | 2023-06-19 | - | 3.045 | 57.19 | - | 3.4 | 52.92 | 660 | 325 | 2.0308 | 116 | 2023-06-19 | - | 5.53 | 55.12 | 1488 | 1425 | 1.0442 | 30 | - | 3.65 | 49.89 | 1320 | 1200 | 1.1 | 30 | 2023-06-19 | - | - | - | - | - | 0 | - |  |  | 340 | 170 | - | -
2023-06-20 | 1 | 12.38 | 13.38 | 807.5321 | 16.569 | 6.88 | 313.9 | 782 | 315 | 52.6 | 72.5 | 6.81 | 269 | 780 | 280 | 6.408 | 49000000 | 4000000 | 2023-06-20 | - | - | - | - | - | 374 | 6.65 | 19 | 11 | 54 | - | 6.82 | 14 | 11.6 | 62 | 15230 | 2023-06-20 | 6.95 | 6.8 | 52 | 13.7 | 6 | 13.4 | 6.9 | 7.3 | 50 | 11.8 | 600 | 250 | 0.2 | 2023-06-20 | 6.82 | 0.4 | 7505 | 4715 | 955 | 127.3951 | 6.665 | 0.39 | 7080 | 4030 | 950 | 134.2307 | 2023-06-20 | 6.535 | 3.6925 | 61.76 | 6.52 | 3.99 | 58.9 | - | 350 | - | 164 | 2023-06-20 | 7.03 | 3.67 | 57.04 | 1608 | 1400 | 1.1486 | 30 | 6.99 | 3.59 | 56.51 | 1620 | 1550 | 1.0452 | 30 | 2023-06-20 | - | - | - | - | - | 62 | - |  |  | 453 | 170 | - | -
2023-06-21 | 1.3 | 11.77 | 13.07 | 736.5455 | 17.745 | 7.02 |  | 940 | 390 | 63.8 | 59.5 | 7.04 | 328.9 | 796 | 360 | 7.109 | 35000000 | 8000000 | 2023-06-21 | 310 | 7.01 | 970 | 328.9 | 840 | 302 | 6.84 | 15 | 12.1 | 50 | 9990 | 6.82 | 16 | 11.5 | 56 | 11390 | 2023-06-21 | 7.24 |  | 48 | 14.7 | 8 | 17.1 | 6.92 | 6.4 | 46 | 10.4 | 510 | 210 | 0.2 | 2023-06-21 | 6.78 | 0.53 | 7395 | 4055 | 940 | 127.1108 | 6.62 | 0.495 | 6625 | 3180 | 910 | 137.4145 | 2023-06-21 | 6.56 | 2.8875 | 59.005 | 6.55 | 4.01 | 55.68 | 966 | 450 | 2.1467 | 197 | 2023-06-21 | 6.87 | 3.72 | 56.91 | 1584 | 1525 | 1.0387 | 30 | 6.98 | 3.46 | 51.41 | 1290 | 1375 | 0.93818 | 30 | 2023-06-21 | 6.84 | 2.4316 | 42.9134 | 19.14 | 52.61 | 158 | - |  |  | - | - | - | -
2023-06-22 | 1 | 11.43 | 12.43 | 672.6554 | 18.479 | 7.11 |  | 1021 | 580 | 33 | 72.5 | 7.19 |  | 926 | 330 | 8.114 | 44000000 | 20000000 | 2023-06-22 | - | 7.04 | 620 |  | 836 | 353 | 7.02 | 20 |  | 50 | 12100 | 6.96 | 16 |  | 48 | 11330 | 2023-06-22 | 6.94 |  | 38 | 14.7 | 8 | 11.5 | 7.11 |  | 46 | 11 | 480 | 80 | 0.6 | 2023-06-22 | 6.875 | 0.51 | 7925 | 4730 | 945 | 119.2555 | 6.84 | 0.655 | 6745 | 4115 | 890 | 133.2927 | 2023-06-22 | 6.5525 | 2.95 | 55.76 | 6.59 | 4.02 | 53.94 | 1086 | 400 | 2.715 | 112 | 2023-06-22 | 7.02 | 3.39 | 48.16 | 1344 | 1600 | 0.84 | 30 | 6.99 | 4.6 | 50.77 | 1566 | 1425 | 1.0989 | 30 | 2023-06-22 | 6.93 | 2.9003 | 49.7041 | 22.05 | 51.71 | 162 | - |  |  | - | - | - | -
2023-06-23 | 1 | 14.42 | 15.42 | 824.4226 | 18.704 | 7.1 |  | 1031 | 520 | 62.7 | 41 | 6.94 |  | 988 | 478 | 7.002 | 50000000 | 3000000 | 2023-06-23 | 345 | 6.9 | 1555 |  | 912 | 356 | 6.82 | 11 |  | 52 | 13150 | 6.73 | 21 |  | 57 | 13480 | 2023-06-23 | 7.18 |  | 50 | 11.3 | 4 | 20.2 | 6.83 |  | 48 | 11.8 | 610 | 200 | 0.5 | 2023-06-23 | 6.795 | 0.4 | 7020 | 3640 | 930 | 133.2707 | 6.68 | 0.685 | 6875 | 3550 | 950 | 138.8806 | 2023-06-23 | 6.5075 | 3.365 | 57.1975 | 6.48 | 3.8 | 53.16 | - | 375 | - | 203 | 2023-06-23 | 7.02 | 4.63 | 43.13 | 1500 | 1425 | 1.0526 | 30 | 6.95 | 3.76 | 47.89 | 1620 | 1400 | 1.1571 | 30 | 2023-06-23 | 7.19 | 2.839 | 51.2097 | 19.36 | 57.79 | 167 | - |  |  | 340 | 170 | - | -
2023-06-24 | 1.2 | 11.93 | 13.13 | 634.6368 | 20.689 | 6.94 |  | 710 | 335 | 45.4 | 19.5 | 7.19 |  | 1023 | 480 | 9.501 | 45000000 | 25000000 | 2023-06-24 | 465 | 7.14 | 1015 |  | 1019 | 409 | 6.82 | 22 |  | 62 | 12200 | 6.86 | 17 |  | 59 | 14230 | 2023-06-24 | 7.5 |  | 31 | 9.7 | 3 | 12 | 6.94 |  | 48 | 11.2 | 710 | 280 | 0.2 | 2023-06-24 | 6.76 | 0.32 | 7270 | 3875 | 935 | 128.8604 | 6.795 | 0.46 | 6870 | 3850 | 955 | 139.3753 | 2023-06-24 | 6.575 | 2.675 | 53.1425 | 6.55 | 3.73 | 53.52 | 624 | 325 | 1.92 | 200 | 2023-06-24 | 7.01 | 4.56 | 44.02 | 1596 | 1425 | 1.12 | 30 | 7.01 | 5.88 | 51.68 | - | 1525 | - | 30 | 2023-06-24 | - | - | - | 21.69 | - | 162 | - |  |  | - | - | - | -
2023-06-25 | 0 | 15.23 | 15.23 | 791.7035 | 19.237 | 7.19 |  | 788 | 240 | 52.6 | 38 | 6.96 |  | 740 | 290 | 8.214 | 50000000 | 3000000 | 2023-06-25 | 275 | 6.86 | 755 |  | 915 | 337 | 6.87 | 11 |  | 57 | 11420 | 6.73 | 8 |  | 46 | 14900 | 2023-06-25 | 7.28 |  | 38 | 13.3 | 7.5 | 14 | 6.99 |  | 26 | 11.8 | 600 | 300 | 0.1 | 2023-06-25 | 6.695 | 0.185 | 7095 | 3190 | 915 | 129.3066 | 6.64 | 0.325 | 6730 | 3120 | 830 | 123.2974 | 2023-06-25 | 6.565 | 3.0725 | 59.855 | 6.58 | 4.3518 | 56.129 | - | 375 | - | 171 | 2023-06-25 | 7.12 | 3.9 | 51.71 | 1374 | 1500 | 0.916 | 31 | 7.03 | 3.66 | 53.3 | 1452 | 1575 | 0.9219 | 30 | 2023-06-25 | 6.97 | 3.0979 | 51.9369 | 22.78 | 48.3 | 166 | - |  |  | - | - | - | -
2023-06-26 | 0 | 17.17 | 17.17 | 850.9689 | 20.177 | - | - | - | - | - | - | 7.25 |  | 844 | 365 | - | - | - | 2023-06-26 | - | 7.32 | 700 |  | 944 | 351 | 7.09 | 20 |  | 61 | 11230 | 6.99 | 14 |  | 56 | 15320 | 2023-06-26 | - | - | - | - | - | - | 7.33 |  | 44 | 8.2 | - | - | 0.2 | 2023-06-26 | 6.785 | 0.205 | 7435 | 3855 | 880 | 118.7768 | 6.765 | 0.335 | 6815 | 3345 | 730 | 107.2398 | 2023-06-26 | 6.6775 | 2.96 | 53.7825 | 6.77 | 3.22 | 55.41 | 660 | 475 | 1.3895 | 200 | 2023-06-26 | 7.28 | 3.57 | 51.03 | 1188 | 1625 | 0.73108 | 31 | 7.17 | 3.67 | 53.24 | - | 1650 | - | 31 | 2023-06-26 | 7.11 | 2.9041 | 52.3577 | 21.71 | 49.61 | 170 | - |  |  | - | - | - | -
2023-06-27 | 0 | 17.13 | 17.13 | 851.6456 | 20.114 | [13 empty] | 2023-06-27 | [16 empty] | 2023-06-27 | [13 empty] | 2023-06-27 | [12 empty] | 2023-06-27 | [10 empty] | 2023-06-27 | [14 empty] | 2023-06-27
2023-06-28 | 0 | 15.13 | 15.13 | 912.8756 | 16.574 | [13 empty] | 2023-06-28 | [16 empty] | 2023-06-28 | [13 empty] | 2023-06-28 | [12 empty] | 2023-06-28 | [10 empty] | 2023-06-28 | [14 empty] | 2023-06-28
2023-06-29 | 0 | 16.11 | 16.11 | 871.5174 | 18.485 | [13 empty] | 2023-06-29 | [16 empty] | 2023-06-29 | [13 empty] | 2023-06-29 | [12 empty] | 2023-06-29 | [10 empty] | 2023-06-29 | [14 empty] | 2023-06-29
2023-06-30 |  |  | 0 | #DIV/0! | [14 empty] | 2023-06-30 | [16 empty] | 2023-06-30 | [13 empty] | 2023-06-30 | [12 empty] | 2023-06-30 | [10 empty] | 2023-06-30 | [14 empty] | 2023-06-30
AVG | 0.98621 | 11.5038 | 12.0737 |  | 17.1886 | 7.0887 | 358.5 | 926.96 | 396.8 | 58.964 | 56 | 7.0775 | 374.2429 | 963.5385 | 415.6923 | 7.882 | 39880000 | 19840000 | AVG | 415.5 | 7.0491 | 980.8333 | 487.9263 | 1007.3333 | 366.3462 | 6.9761 | 17 | 13.54 | 55.08 | 10935.4167 | 6.9461 | 22.76 | 16.78 | 68.68 | 12332.8 | AVG | 7.2539 | 12.075 | 50.4 | 16.188 | 6.42 | 16.152 | 7.0933 | 11.3571 | 51 | 14.7192 | 536.4 | 179.6 | 0.24231 | AVG | 6.8478 | 0.4656 | 7032.8 | 4219.3478 | 936.4 | 134.4285 | 6.7704 | 0.4896 | 6808.4 | 4040.1304 | 904.2 | 134.5095 | AVG | 6.6661 | 3.1675 | 56.3897 | 6.6543 | 3.6077 | 55.1296 | 745.3 | 406.44 | 1.9311 | 138.6923 | AVG | 7.0609 | 3.7368 | 51.2164 | 1560.48 | 1478 | 1.0599 | 29.0769 | 7.0026 | 3.7928 | 51.2492 | 1593.913 | 1437 | 1.1231 | 29.0385 | AVG | 7.011 | 3.005 | 49.826 | 21.9495 | 51.9357 | 144.0385 |  |  |  | 464.3 | 180.95
Remarks:POWER CUT ON JUNE 13TH | [18 empty] | Remarks: POWER CUT ON JUNE 13TH | [16 empty] | Remarks: POWER CUT ON JUNE 13TH | [13 empty] | Remarks: POWER CUT ON JUNE 13TH | [12 empty] | Remarks: POWER CUT ON JUNE 13TH | [10 empty] | Remarks: POWER CUT ON JUNE 13TH | [14 empty] | Remarks: POWER CUT ON JUNE 13TH
*BDL - Below Detectable Limit, ([-] - analysis not conducted) | [18 empty] | *BDL - Below Detectable Limit | [16 empty] | *BDL - Below Detectable Limit | [13 empty] | *BDL - Below Detectable Limit | [12 empty] | *BDL - Below Detectable Limit | [10 empty] | *BDL - Below Detectable Limit | [14 empty] | *BDL - Below Detectable Limit
VA TECH WABAG | [14 empty] | PID | KVWSMB |  |  | VA TECH WABAG | [7 empty] | PID |  |  |  |  | KVWSMB |  |  |  | VA TECH WABAG | [9 empty] | PID | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  | KVWSMB |  |  |  | VA TECH WABAG |  |  |  |  | PID |  |  | KVWSMB |  |  | VA TECH WABAG |  |  |  |  | PID |  |  |  |  | KVWSMB |  |  |  |  | VA TECH WABAG | [9 empty] | PID |  | KVWSMB
CHEMIST |  |  |  |  | PLANT INCHARGE | [6 empty] | PLANT INCHARGE | [6 empty] | CHEMIST |  | PLANT INCHARGE | [14 empty] | CHEMIST | [7 empty] | PLANT INCHARGE | [5 empty] | CHEMIST |  | PLANT INCHARGE | [10 empty] | CHEMIST |  | PLANT INCHARGE | [8 empty] | CHEMIST |  | PLANT INCHARGE | [12 empty] | CHEMIST |  |  | PLANT INCHARGE
Formulas:
Date = [Date]
Aeration Tank = [Date]
Digester Sludge Feeding Details = [Aeration Tank]
Digester Performance Details = [Digester Sludge Feeding Details]
Digester Outlet = [Digester Performance Details]